## 동력설비부하계산서
동력설비 부하계산서
기기번호 | 기기명 | 사양 | 동력 (kW) | 기동방식 | 효율 (η) | 역률 (COSΘ) | 정격전압 (V) | 부하용량 (kVA) | 전류 |  | 상용 |  |  |  | 수용율 (%) | 조작반 | 비고
[9 empty] | 정격전류 (A) | 상용전류 (A) | 상용 | 예비 | 동력 (kW) | 부하 (kVA)
MCC1 | [9 empty] | 82.3
M-101 | treatment tank mixer | 형식 : 수중횡축 프로펠러형 (인양장치, 모니터링유니트 포함) 규격 : 110.00 ㎥ | 1.5 | 직입 | 0.865 | 0.9 | 380 | 1.9268 | 2.9275 | 5.8551 | 2 | 0 | 3 | 3.8536 | 60 | LOP | MCC 상세 설계 필요
M-102 | treated water transfer pump | 형식 : 스프르트펌프 규격 : 9.00 ㎥/min × 7.50 kW | 7.5 | 직입 | 0.917 | 0.9 | 380 | 9.0876 | 13.8076 | 27.6152 | 2 | 1 | 15 | 18.1752 | 80 | LOP
M-103 | treated water transfer pump | 형식 : 스프르트펌프 규격 : 9.00 ㎥/min × 7.50 kW | 7.5 | 직입 | 0.917 | 0.9 | 380 | 9.0876 | 13.8076 | 27.6152 | 2 | 1 | 15 | 18.1752 | 80 | LOP
M-202 | POLYMER DISSOLUTION DEVICE | 형식 : 분말 연속용해 공급장치 규격 : 1.00 kg/h | 1.3 | MOP | 0.865 | 0.9 | 380 | 1.6699 | 2.5372 | 2.5372 | 1 | 0 | 1.3 | 1.6699 | 60 | MOP
M-203 | POLYMER SUPPLY PUMP | 형식 : 일축스크류(모노)펌프(VVVF) 규격 : 0.45 ㎥/h × 0.40 kW | 0.4 | 인버터 | 0.65 | 0.9 | 380 | 0.68376 | 1.0389 | 2.0778 | 2 | 1 | 0.8 | 1.3675 | 80 | LOP
M-204 | CONVEYOR | 형식 : 무주축 스크류 컨베이어 규격 : 250.00 mm | 1.5 | 직입 | 86.5 | 0.9 | 380 | 0.019268 | 0.029275 | 0.029275 | 1 | 0 | 1.5 | 0.019268 | 60 | LOP
M-205 | CAKE HOPPER | 형식 : 유압식 케익호퍼 규격 : 10.00 ㎥ | 7.5 | MOP | 0.917 | 0.9 | 380 | 9.0876 | 13.8076 | 13.8076 | 1 | 0 | 7.5 | 9.0876 | 60 | MOP

## 부하일람표
부하 일람표
No | 부하명 | 정격전압 (V) | 상용동력 (kW) | 상용부하 (kVA) | 수용율 (%) | 수용동력 (kW) | 수용부하 (kVA) | 비고
1 | MCC1 | 380 | 44.1 | 52.35 | 68.6 | 30.25 | 35.91
2 | 건축설비 분전반 | 380 | 52.35 | 52.35 | 100 | 52.35 | 52.35

## 동력설비리스트
동력설비 리스트
기기번호 | 기기명 | 사양 | 동력 (kW) | 기동방식 | 정격전류 (A) | 수량 |  |  | 전선 |  | PLC전선 | [6 empty] | 전선외경 |  |  |  | 차단기 | MC | EOCR | 인버터 | 콘덴서 | 소프트스타터 | 기준거리 | MCC사이즈
|  |  | (kW) |  | (A) | 상용 | 예비 | 계 | CV | GV | DI | DO | AI | AO | 485통신 | CVV | CVV SB | CV | GV | CVV | CVV SB | [6 empty] | (m) | (mm)
MCC1
| MCC1 |  | 36.29 | - | 82.3 | 1 | 0 | 1 | 35SQ 4C | 16SQ | - | - | - | - | - | - | 1.5SQ 2C | 28.00mm | 10.00mm | - | 12.00mm | ABS 104/100 | - | - | - | - | - | 30M | 600mm
M-101 | treatment tank mixer | 형식 : 수중횡축 프로펠러형 (인양장치, 모니터링유니트 포함) 규격 : 110.00 ㎥ | 1.5 | 직입 | 2.93 | 2 | 0 | 2 | 4SQ 3C | 4SQ | 5 | 1 | - | - | - | 1.5SQ 8C | - | 13.50mm | 8.00mm | 15.50mm | - | ABS 33/3 | MC-6a | DMP06i-TZ | - | 10μF | - | 18M | 200mm
M-102 | treated water transfer pump | 형식 : 스프르트펌프 규격 : 9.00 ㎥/min × 7.50 kW | 7.5 | 직입 | 13.81 | 2 | 1 | 3 | 4SQ 3C | 4SQ | 3 | 1 | - | - | - | 1.5SQ 6C | - | 13.50mm | 8.00mm | 14.50mm | - | ABS 33/15 | MC-18a | DMP60i-TZ | - | 75μF | - | 31M | 300mm
M-103 | treated water transfer pump | 형식 : 스프르트펌프 규격 : 9.00 ㎥/min × 7.50 kW | 7.5 | 직입 | 13.81 | 2 | 1 | 3 | 4SQ 3C | 4SQ | 3 | 1 | - | - | - | 1.5SQ 6C | - | 13.50mm | 8.00mm | 14.50mm | - | ABS 33/15 | MC-18a | DMP60i-TZ | - | 75μF | - | 31M | 300mm
M-202 | POLYMER DISSOLUTION DEVICE | 형식 : 분말 연속용해 공급장치 규격 : 1.00 kg/h | 1.3 | MOP | 2.54 | 1 | 0 | 1 | 4SQ 4C | 4SQ | - | - | - | - | 1 | - | 1.5SQ 2C | 14.50mm | 8.00mm | - | 12.00mm | EBS 34/3 | - | - | - | - | - | 39M | 200mm
M-203 | POLYMER SUPPLY PUMP | 형식 : 일축스크류(모노)펌프(VVVF) 규격 : 0.45 ㎥/h × 0.40 kW | 0.4 | 인버터 | 1.04 | 2 | 1 | 3 | 4SQ 3C | 4SQ | 3 | 1 | - | - | - | 1.5SQ 6C | - | 13.50mm | 8.00mm | 14.50mm | - | ABS 33/3 | - | - | G100 0.75 | - | - | 35M | 400mm
M-204 | CONVEYOR | 형식 : 무주축 스크류 컨베이어 규격 : 250.00 mm | 1.5 | 직입 | 0.03 | 1 | 0 | 1 | 4SQ 3C | 4SQ | 3 | 1 | - | - | - | 1.5SQ 6C | - | 13.50mm | 8.00mm | 14.50mm | - | ABS 33/3 | MC-6a | DMP06i-TZ | - | 10μF | - | 47M | 200mm
M-205 | CAKE HOPPER | 형식 : 유압식 케익호퍼 규격 : 10.00 ㎥ | 7.5 | MOP | 13.81 | 1 | 0 | 1 | 4SQ 4C | 4SQ | - | - | - | - | - | - | - | 14.50mm | 8.00mm | - | - | EBS 34/15 | - | - | - | - | - | 46M | 200mm

## 계측기리스트
계측기 리스트
태그 | 번호 | 계측기명 | 설치위치 | 측정대상물질 | 수량 | 전선 |  | PLC전선 | [6 empty] | 전선외경 |  |  |  | 비고
[6 empty] | CV | GV | DI | DO | AI | AO | 485통신 | CVV | CVV SB | CV | GV | CVV | CVV SB
1.TreatmentTank
LIT | 1001 | 레이더식 수위계 | {con1_name} | Raw water | 1 | 2.5SQ 3C | 4SQ | - | - | 1 | - | - | - | 1.5SQ 2C | 12.50mm | 8.00mm | - | 12.00mm | 필요 시, 전선 및 PLC 전선 통합 가능
2.Dewatering
FIT | 2301 | 전자식 유량계 | POLYMER SUPPLY PUMP DISCHARGE SIDE | Chemical | 2 | 2.5SQ 3C | 4SQ | 1 | - | 1 | - | - | - | 1.5SQ 4C | 12.50mm | 8.00mm | - | 13.50mm | 필요 시, 전선 및 PLC 전선 통합 가능
FIT | 2101 | 전자식 유량계 | DEHYDRATOR SUCTION SIDE | Sludge | 2 | 2.5SQ 3C | 4SQ | 1 | - | 1 | - | - | - | 1.5SQ 4C | 12.50mm | 8.00mm | - | 13.50mm

## LOP면수산출서
LOP 면수 산출서
기기번호 | 기기명 | LOP 면수 | 비고
MCC1
M-101A | treatment tank mixerA | IS1-M(LOP 1회로) | 옥외 설치 시, IS 대신 OS 사용
M-101B | treatment tank mixerB | IS1-M(LOP 1회로)
M-102A | treated water transfer pumpA | IS1-M(LOP 1회로)
M-102B | treated water transfer pumpB | IS1-M(LOP 1회로)
M-102C | treated water transfer pumpC | IS1-M(LOP 1회로)
M-103A | treated water transfer pumpA | IS1-M(LOP 1회로)
M-103B | treated water transfer pumpB | IS1-M(LOP 1회로)
M-103C | treated water transfer pumpC | IS1-M(LOP 1회로)
M-203A | POLYMER SUPPLY PUMPA | IS1-M(LOP 1회로)
M-203B | POLYMER SUPPLY PUMPB | IS1-M(LOP 1회로)
M-203C | POLYMER SUPPLY PUMPC | IS1-M(LOP 1회로)
M-204A | CONVEYORA | IS1-M(LOP 1회로)

## IO MCC
IO MCC
기기번호 | 기기명 | Status & Signal | PLC전선 | [5 empty] | 케이블 산출 |  |  | 비고
|  |  | DI | DO | AI | AO | RS 485 | Ethernet | CV | CVV | CVV-SB
MCC1 | MCC1 | DI : RE / RUN / FA | - | - | - | - | - | - | 35SQ 4C | - | 1.5SQ 2C
M-101A | treatment tank mixerA | DI : RE / RUN / FA(에러) / FA(누수) / FA(과열), DO : START | 5 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 8C | -
M-101B | treatment tank mixerB | DI : RE / RUN / FA(에러) / FA(누수) / FA(과열), DO : START | 5 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 8C | -
M-102A | treated water transfer pumpA | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-102B | treated water transfer pumpB | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-102C | treated water transfer pumpC | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-103A | treated water transfer pumpA | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-103B | treated water transfer pumpB | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-103C | treated water transfer pumpC | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-202 | POLYMER DISSOLUTION DEVICE | DI : RE / RUN / FA | - | - | - | - | 1 | - | 4SQ 4C | - | 1.5SQ 2C
M-203A | POLYMER SUPPLY PUMPA | - | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-203B | POLYMER SUPPLY PUMPB | - | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-203C | POLYMER SUPPLY PUMPC | - | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-204 | CONVEYOR | DI : RE / RUN / FA | 3 | 1 | - | - | - | - | 4SQ 3C | 1.5SQ 6C | -
M-205 | CAKE HOPPER | - | - | - | - | - | - | - | 4SQ 4C | - | -
계 | - | - | 40 | 12 | 0 | 0 | 1 | 0 | - | - | -

## IO 계측제어
IO 계측제어
계측기명 |  | Status & Signal | PLC전선 | [5 empty] | 케이블 산출 |  |  | 비고
태그번호 | 계측기명 |  | DI | DO | AI | AO | RS 485 | Ethernet | CV | CVV | CVV-SB
1)TreatmentTank
LIT-1001 | 레이더식 수위계 | AI : 4~20mA | - | - | 1 | - | - | - | 2.5SQ 3C | - | 1.5SQ 2C | 필요 시,전선 및 PLC 전선 통합 가능
2)Dewatering
FIT-2301A | 전자식 유량계A | AI : 4~20mA, DI : 적산 | 1 | - | 1 | - | - | - | 2.5SQ 3C | - | 1.5SQ 4C | 필요 시,전선 및 PLC 전선 통합 가능
FIT-2301B | 전자식 유량계B | AI : 4~20mA, DI : 적산 | 1 | - | 1 | - | - | - | 2.5SQ 3C | - | 1.5SQ 4C
FIT-2101A | 전자식 유량계A | AI : 4~20mA, DI : 적산 | 1 | - | 1 | - | - | - | 2.5SQ 3C | - | 1.5SQ 4C
FIT-2101B | 전자식 유량계B | AI : 4~20mA, DI : 적산 | 1 | - | 1 | - | - | - | 2.5SQ 3C | - | 1.5SQ 4C
계 | - | - | 4 | 0 | 5 | 0 | 0 | 0 | - | - | -

## IO 집계표
IO 집계표
항목 구분 |  | Digital |  | Analog |  | 통신 |  | 계 | 비 고
|  | DI | DO | AI | AO | RS-485 | Ethernet
MCC | SBR Actual | 40 | 12 | 0 | 0 | 1 | 0 | 53
계측제어 |  | 4 | 0 | 5 | 0 | 0 | 0 | 9
Total | Actual | 44 | 12 | 5 | 0 | 1 | 0 | 62
| Install(20%) | 53 | 15 | 6 | 0 | 2 | 0 | 76
| Card 수량 | 2 | 1 | 1 | 0 | 1 | 0 | 5
* Point/Card | DI : | 32 | Point
| DO : | 32 | Point
| AI : | 8 | Point
| AO : | 8 | Point
| COMM : | 2 | Point
* Install = Actual × 1.2 (20%)

## 케이블스케쥴(동력)
케이블스케쥴(동력)
케이블번호 | 기기명 | FROM | TO | 전선 | 접지선 | 전선 외경 |  |  | 전선관 | 비고
[6 empty] | CV | GV | 단면적
MCC1
MCC1 | MCC1 FEEDER | MCCB | MCC1 | 0.6/1kV F-CV 35SQ 4C | 16SQ | 28.00mm | 10.00mm | 694 | 54C
M-101A | treatment tank mixerA | MCC1 | M-101A | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-101B | treatment tank mixerB | MCC1 | M-101B | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-102A | treated water transfer pumpA | MCC1 | M-102A | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-102B | treated water transfer pumpB | MCC1 | M-102B | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-102C | treated water transfer pumpC | MCC1 | M-102C | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-103A | treated water transfer pumpA | MCC1 | M-103A | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-103B | treated water transfer pumpB | MCC1 | M-103B | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-103C | treated water transfer pumpC | MCC1 | M-103C | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-202 | POLYMER DISSOLUTION DEVICE | MCC1 | M-202 | 0.6/1kV F-CV 4SQ 4C | 4SQ | 14.50mm | 8.00mm | 215 | 36C
M-203A | POLYMER SUPPLY PUMPA | MCC1 | M-203A | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-203B | POLYMER SUPPLY PUMPB | MCC1 | M-203B | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-203C | POLYMER SUPPLY PUMPC | MCC1 | M-203C | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-204 | CONVEYOR | MCC1 | M-204 | 0.6/1kV F-CV 4SQ 3C | 4SQ | 13.50mm | 8.00mm | 193 | 28C
M-205 | CAKE HOPPER | MCC1 | M-205 | 0.6/1kV F-CV 4SQ 4C | 4SQ | 14.50mm | 8.00mm | 215 | 36C

## 케이블스케쥴(제어)
케이블스케쥴(제어)
케이블번호 | 기기명 | FROM | TO | 전선 | 전선 외경 |  | 전선관 | 비고
[5 empty] | CVV/CVV-SB | 단면적
MCC1
MCC1 | MCC1 FEEDER | PLC | MCC1 | F-CVV-SB 1.5SQ 2C | 12.00mm | 113 | 22C
M-101A | treatment tank mixerA | PLC | M-101A | F-CVV 1.5SQ 8C | 15.50mm | 188 | 28C
M-101B | treatment tank mixerB | PLC | M-101B | F-CVV 1.5SQ 8C | 15.50mm | 188 | 28C
M-102A | treated water transfer pumpA | PLC | M-102A | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-102B | treated water transfer pumpB | PLC | M-102B | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-102C | treated water transfer pumpC | PLC | M-102C | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-103A | treated water transfer pumpA | PLC | M-103A | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-103B | treated water transfer pumpB | PLC | M-103B | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-103C | treated water transfer pumpC | PLC | M-103C | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-202 | POLYMER DISSOLUTION DEVICE | PLC | M-202 | F-CVV-SB 1.5SQ 2C | 12.00mm | 113 | 22C
M-203A | POLYMER SUPPLY PUMPA | PLC | M-203A | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-203B | POLYMER SUPPLY PUMPB | PLC | M-203B | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-203C | POLYMER SUPPLY PUMPC | PLC | M-203C | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C
M-204 | CONVEYOR | PLC | M-204 | F-CVV 1.5SQ 6C | 14.50mm | 165 | 28C

## 케이블스케쥴(계측)
케이블스케쥴(계측)
케이블번호 | 기기명 | FROM | TO | 전선 | 접지선 | 전선 외경 |  |  | 전선관 | 비고
[6 empty] | CV/CVV-SB | GV | 단면적
1. TreatmentTank
LIT-1001 | 레이더식 수위계 | PLC | LIT-1001 | 0.6/1kV F-CV 2.5SQ 3C | 4SQ | 12.50mm | 8.00mm | 172 | 28C | 필요 시,전선 및 PLC 전선 통합 가능
LIT-1001 | 레이더식 수위계 | LIT-1001 | PLC | F-CVV-SB 1.5SQ 2C | - | 12.00mm | - | 113 | 22C
2. Dewatering
FIT-2301 A | 전자식 유량계 A | PLC | FIT-2301 A | 0.6/1kV F-CV 2.5SQ 3C | 4SQ | 12.50mm | 8.00mm | 172 | 28C | 필요 시,전선 및 PLC 전선 통합 가능
FIT-2301 A | 전자식 유량계 A | FIT-2301 A | PLC | F-CVV-SB 1.5SQ 4C | - | 13.50mm | - | 143 | 28C
FIT-2301 B | 전자식 유량계 B | PLC | FIT-2301 B | 0.6/1kV F-CV 2.5SQ 3C | 4SQ | 12.50mm | 8.00mm | 172 | 28C
FIT-2301 B | 전자식 유량계 B | FIT-2301 B | PLC | F-CVV-SB 1.5SQ 4C | - | 13.50mm | - | 143 | 28C
FIT-2101 A | 전자식 유량계 A | PLC | FIT-2101 A | 0.6/1kV F-CV 2.5SQ 3C | 4SQ | 12.50mm | 8.00mm | 172 | 28C
FIT-2101 A | 전자식 유량계 A | FIT-2101 A | PLC | F-CVV-SB 1.5SQ 4C | - | 13.50mm | - | 143 | 28C
FIT-2101 B | 전자식 유량계 B | PLC | FIT-2101 B | 0.6/1kV F-CV 2.5SQ 3C | 4SQ | 12.50mm | 8.00mm | 172 | 28C
FIT-2101 B | 전자식 유량계 B | FIT-2101 B | PLC | F-CVV-SB 1.5SQ 4C | - | 13.50mm | - | 143 | 28C